VALVES APPLICATIONS

| Place/Industry | Common Valve Types | Usage Purpose |
| --- | --- | --- |
| Water treatment & supply | Butterfly (double flanged, lug type), Gate, Globe, Ball | Flow control, isolation, pressure regulation |
| HVAC & Building Systems | Butterfly (concentric, resilient seated), Ball, Globe | Heating, cooling, and ventilation flow regulation |
| Fire Protection & Air/Gas | Plug, Ball, Butterfly | Isolation and control for safety and gas systems |
| Power Plants & Steam Systems | Globe, Gate, Butterfly | Steam and cooling water flow control and regulation |
| Chemical, Pharma & Food | Diaphragm, Pinch, Resilient seated Butterfly | Sanitary flow control, precise throttling |
| Shipbuilding & Marine | Globe, Ball, Gate, Diaphragm, Butterfly | Fuel, water, and fluid system control on board |
| Oil and Gas | Ball, Gate, Plug, Check | Pipeline flow control and shutoff under high pressure and corrosive fluids |

REPLACEMETS POSSIBLE IN WATER SYSTEM

| Original Valve Type | Can Replace With | Conditions When Feasible | When Not Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Gate Valve | Ball Valve (full port), Butterfly (limited), Plug Valve | ≤50mm diameter, ≤PN40 pressure, clean water, infrequent operation, full open/close duty | Large diameter >50mm with butterfly, high pressure (PN >40), frequent throttling, slurry/sewage, pump discharge, precise pressure regulation | Lowest pressure drop, PN up to 100, ball valves better for frequent cycles, butterfly increases pressure drop and risk of water hammer |
| Ball Valve (Full Port) | Gate Valve, Butterfly Valve (limited), Plug Valve | ≤PN40 systems, frequent on/off cycling, control/isolation duty, space-restricted installation | Pump discharge or high-pressure surge >PN40, gravity-fed high pressure, large diameter >150mm, throttling service, slurry/wastewater | Cost increases with size; full-port ball valves minimize pressure drop; not suitable for throttling or slurry |
| Butterfly Valve | Ball Valve (high cost), Gate Valve (≤PN40), Plug Valve | PN ≤40, space-constrained installations, <100mm diameter preferred, automated, frequent operation, low-solid water | High-pressure systems >PN40, pump discharge, high-temperature water >50°C, water hammer-prone, sewage/slurry, pressure regulation | Pressure drop 2-3x higher than gate; risk of water hammer; elastomer limits temperature; major installation if upgrading |
| Check Valve (Swing Type) | Lift Check Valve, Spring Loaded Check Valve | Pressure drop ±10% tolerance, horizontal installation, flow >0.5 m/s, clean/low solids water, pump discharge protection | Vertical installation, flow <0.3 m/s, abrasive slurry, low-pressure systems, high-frequency pulsations, sewage with debris | Swing check preferred for low pressure drop; spring check compact but higher maintenance; material compatibility critical |
| Control Valve (Regulating) | None (direct replacement), Gate Valve + Pressure Regulator | Temporary repairs, system redesign allowing separate control valve, pilot-operated replacements | Direct replacement with ON/OFF valves, field modifications, wrong pressure range, combining check and regulator functions | Specialized for regulation; gate/ball cannot replicate modulation; maintenance intensive; synergy with relief valves needed |
| Globe Valve | Gate Valve (on/off only), Ball Valve (on/off), Butterfly Valve (limited) | Operation changed to full on/off, ≤PN40 with frequent operation, manual control stations | Maintaining throttling/flow control, high velocity >3 m/s, pump suction, automatic actuated lines | Designed for flow modulation, higher pressure drop; partial replacement loses flow control; installation orientation matters |
| Plug Valve | Ball Valve, Gate Valve (isolation), 4-Way to 3-Way Plug Valve | ≤PN40, on/off isolation, clean municipal lines, small bore <50mm, multi-port switching | Pressure >PN40, partial flow throttling, sewage/slurry, system auto-shut with variable torque, reducing ports requires redesign | Quick quarter-turn operation; lubrication critical; can seize unused; ball valve more standardized and economical |

REPLACEMETS POSSIBLE FOR HVAC & BUILDING SYSTEMS

| Original Valve Type | Can Replace With | Conditions When Replacement Is Feasible | When Replacement Is Not Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Gate Valve | Ball Valve (full port), Globe Valve (on/off), Butterfly Valve (large diameter) | Isolation duty in low to moderate pressure systems, ≤PN25, clean water lines | Frequent throttling, HVAC control loops (globe preferred), on/off cycling >50/day | Gate valves offer low pressure drop, economical for shutoff; ball valves better for repeated operation |
| Ball Valve | Gate Valve, Butterfly Valve (limited) | Full bore isolation, ≤PN25, lower flow velocity HVAC lines, domestic water | Throttling service, high cycle continuous operation, dirty water | Ball valves provide quick quarter-turn operation; plastic ball valves available for potable water |
| Globe Valve | Control Valve (automated), Needle Valve | Control of flow and pressure, heating loops, chilled water, steam control | On/off isolation without flow control; use gate or ball for shutoff | Globe valves preferred for modulation; should be sized per Cv and have corrosion-resistant stem and seat |
| Butterfly Valve | Ball Valve (for isolation), Gate Valve (low pressure) | Large pipe sizes, low pressure chilled water loops, fire sprinkler isolation | Steam lines, throttling, tight shutoff requirements | Butterfly valves low cost and compact; rubber seats limit temperature; triple offset types for full shutoff |
| Check Valve (lift/swing) | Wafer or Spring Check Valve | Backflow prevention on pump discharge, system protection | Vertical upward flow with swing check, pulsating flow | Check valves essential for preventing pump damage; material choice critical for corrosion resistance |
| Pressure Relief Valve | Same type and rating valve | Safety valve replacement in boilers, chilled water systems | Improper sizing or replacing safety valves with manual isolation valves | Must comply with ASME, ANSI safety codes; testing and certification required |
| Diaphragm Valve | Globe Valve, Ball Valve (isolation only) | For potable water systems requiring sanitary design | High pressure, high temperature, or abrasive fluids | Diaphragm valves excellent for leak-proof isolation in potable water; elastomer compatibility critical |
| Solenoid Valve | Motorized Ball Valve, Zone Valve | Automated zone control, quick on/off action in heating/cooling zones | High-temperature steam or abrasive service | Solenoid valves must be rated for temperature and media; wiring and control integration important |
| Plug Valve | Ball Valve, Butterfly Valve (limited) | Low-pressure isolation with minimal pressure drops | Dirty water, steam, or throttling | Plug valves fast operation, but maintenance intensive in dirty media |

REPLACEMETS POSSIBLE FOR FIRE PROTECTION & AIR/GAS

| Original Valve Type | Can Replace With | Conditions When Replacement Is Feasible | When Replacement Is Not Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Gate Valve | Ball Valve (full port), Butterfly Valve (marine/spec) | Isolation in sprinkler mains, ≤PN40, clean dry air or water, infrequent operation | Frequent cycling, throttling services, emergency shutoff requiring rapid action | Gate valves standard for sprinkler isolation, ball valves gaining acceptance; butterfly limited for large diameter lines only |
| Ball Valve | Gate Valve, Butterfly Valve (full bore) | Full bore shutoff in compressed air and gas distribution, clean dry gases | Throttling or pressure regulation, dirty/contaminated gases | Ball valve preferred for quick on/off in compressed air systems; must have fire-safe packing for fuel gases |
| Butterfly Valve | Ball Valve, Gate Valve (if large diameter) | Large diameter compressed air or inert gas lines, non-critical pressure drop | On/off fuel gas isolation, throttling, high-pressure oxygen lines | Triple-offset metal seated butterfly valves preferred for tight shutoff in critical systems |
| Check Valve | Lift, Swing, Dual Plate Check Valve | Backflow prevention on air compressor discharge, fuel gas, inert gas lines | Vertical upward flow with swing check, fluctuating pulsation flows | Prevents backflow damage in compressors and pipelines; material selection critical for gas compatibility |
| Pressure Relief Valve | Same rated Safety Relief Valve | Certified safety valve replacement on pneumatic systems, gas storage | Using isolation valves or undersized relief valves | Relief valves safety critical; must be certified to NFPA, ASME codes with documented proof testing |
| Ball Valve (Fire Gas Lines) | Fire-Safe Ball Valve, Gate Valve | Fuel gas isolation in fire suppression systems, fire gas shutoff valves | Throttling or automated flow control; butterfly valves without fire certification | Fire-safe valves with secondary seals prevent leaks during fire conditions, certification mandatory |
| Control Valve | Globe Valve (automated), Needle Valve | Control of gas flow rate, pressure modulation in HVAC or process gas lines | Use of isolation valves in modulating service | Automated control valves sized for minimal pressure drop, low noise; material must meet gas compatibility |
| Solenoid Valve | Pneumatic Actuated Ball Valve | Automated gas or air zone control with quick actuation | Manual operation-only service lines, non-energized emergency systems | Solenoid coils must be explosion proof (ATEX/IECEx) certified in hazardous areas |
| Plug Valve | Ball Valve, Butterfly Valve (limited) | On/off isolation of clean compressed air systems, inert gas lines | Dirty gas, abrasive particles, throttling services | Plug valves fast but rare in fire/gas; lubrication and maintenance critical |

REPLACEMETS POSSIBLE FOR POWER PLANT AND STEAM SYSTEM

| Original Valve Type | Can Replace With | Conditions When Replacement Is Feasible | When Replacement Is NOT Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Gate Valve (steam line isolation) | Pressure Seal Gate, Parallel Slide Gate, Ball Valve (high-temp, full-bore) | On/off isolation only, same or higher pressure class (ASME 150–2500), same temperature rating, clean dry steam, adequate space for actuator | For throttling or flow control, wet steam with carryover erosion, quick-cycling duty, using soft-seated ball at high temp | Gate valves are standard for main steam isolation; full-bore ball possible but must be metal-seated and high-temp rated. |
| Globe Valve (control / throttle) | Globe Control Valve (actuated), Angle Globe Valve | When maintaining throttling function, same flow coefficient (Cv) class, matched pressure/temperature, compatible trim material | Replacing with gate/ball for control duty, high differential pressure without anti-cavitation trim, dirty steam with solids | Globe is preferred for control in steam; body/trim must handle high dp, flashing, noise, and erosion. |
| Ball Valve (aux steam / drains) | High-temp Metal Seated Ball, Gate Valve (isolation), Plug Valve | On/off isolation on auxiliary steam, condensate, or feedwater, ASME class match, temp within ball seat rating, non-throttling duty | Saturated/high superheated main steam above seat rating, throttling, flashing across valve, erosive wet steam | Use metal-seated designs for hot, dirty steam; soft seats (PTFE) unsuitable for high steam temperatures. |
| Butterfly Valve (large bore, LP) | Triple-Offset Metal-Seated Butterfly, Gate Valve | Low/medium pressure steam or hot water, large diameters, where some pressure drop acceptable, triple-offset type for tight shutoff | High-pressure main steam, severe throttling at high ΔP, high cycling at extreme temps, safety-critical isolation | Triple-offset butterfly used for large HRSG/LP steam lines; verify torque, temperature, and seat metallurgy. |
| Check Valve (non-return on steam) | Spring-Loaded Piston Check, Tilting Disc Check | Same direction and orientation, correct cracking pressure, compatible with steam temp/pressure | Using swing check on vertical upflow steam, reverse flow cycling, water hammer zones without damping | NRVs are safety-critical for turbine protection and boiler backflow; sizing for velocity and dp is essential. |
| Safety/Relief Valve (boiler, superheater) | Same type and capacity, higher set pressure only if code-recalculated | Direct replacement with equal or higher certified capacity, same or suitable set pressure, code stamp (ASME I/VIII), correct blowdown | Replacing with isolation or control valve, undersized or uncertified relief, changing set pressure without design review | Never substitute SRVs with other valve types; must follow boiler and pressure vessel codes. |
| Control Valve (steam pressure/flow) | Globe Control Valve with proper trim, Angle Control Valve | Process control duty with defined rangeability, correct Cv, anti-cavitation/noise trim, actuator sized for dp and fail-safe position | Replacing by manual globe/gate, wrong trim for flashing/critical flow, using ball/butterfly for fine modulation | Sizing and trim selection are critical to avoid cavitation, noise, and erosion in steam service. |
| Blowdown Valve (boiler) | Needle/Angle Blowdown Valve, High-pressure Globe Valve | Intermittent, high-velocity discharge from drum, erosion-resistant trim, same pressure class, manual or automated sequencing | Generic gate/ball without erosion-resistant trim, continuous throttling on standard gate, undersized discharge line | Blowdown valves see severe erosive service; use hardened trim and angles to direct jet away from seat. |

REPLACEMETS POSSIBLE FOR CHEMICAL, PHARMA & FOOD

| Original Valve Type | Can Replace With | Conditions When Feasible | When Replacement Is NOT Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Ball Valve (sanitary/full bore) | Sanitary Butterfly Valve, Diaphragm Valve (limited) | Clean, low-viscosity fluids; full bore flow; CIP-compatible materials (316SS) | For viscous, shear-sensitive fluids; high purity sterile processes needing zero dead leg | Ball valves widely used for isolation; should have FDA-compliant seals; be careful replacing with butterfly in sterile lines |
| Butterfly Valve (sanitary, wafer or lug) | Sanitary Ball Valve, Diaphragm Valve | Large-diameter, low-pressure systems; clean fluids; non-sterile non-throttling duty | High-purity sterile lines; shear-sensitive products; critical throttling; pressure >10 bar | Butterfly valves best for large-diameter, low-pressure isolation; triple-offset for tight shutoff in pharma/pharma sterile lines |
| Diaphragm Valve | Sanitary Ball Valve (only isolation), Needle Valve (throttling) | Low flow rates; high purity; sterile environments; acids/alkalis compatibility | High pressure/temperature; abrasive fluids; high speed cycling | Diaphragm valves allow zero dead leg, excellent hygienic design; limited pressure/temperature; elastomers require compatibility |
| Globe Valve (sanitary/control) | Control Valve (automated globe), Needle Valve | When precise throttling/modulation required, compatible materials | On/off only duty; high viscosity or slurries | Globe valves preferred for flow control; ensure hygienic finishes; cleanability critical |
| Check Valve (lift or swing) | Silent Check Valve, Wafer Check Valve | Suitable media; correct orientation; sanitary design | Vertical upward flow without proper design; shear-sensitive fluids | Prevent backflow; bid service possible with silent checks; material corrosion resistance and CIP cleanability important |
| Pinch Valve | Diaphragm Valve, Butterly Valve (limited) | Slurry, viscous fluids, shear sensitive; low pressure | High pressure/temperature systems; precise throttling | Pinch valves protect product integrity with no internal contact; elastomer sleeves must be chemically compatible and replaceable |
| Plug Valve | Ball Valve, Butterly Valve (limited) | Low erosion, on/off use; clean fluids | Abrasive fluids, sterile fluid paths, critical flow control | Plug valves quick quarter turn, but limited hygienic design; lubrication mandatory |
| Control Valve (automated) | Globe Valve with hygienic trim, Needle Valve, Diaphragm Valve (low pressure) | Critical flow control and pressure regulation; compatible with process media | Replacing with simple gate or ball valve for control | Automated control valves must have sanitary design; pressure drop, cavitation, noise must be managed |

REPLACEMETS POSSIBLE FOR MARINE

| Original Valve Type | Can Replace With | Conditions When Replacement Is Feasible | When Replacement Is Not Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Ball Valve (marine rated) | Flanged/wafer Gate Valve, Butterfly Valve (marine specification) | On/off isolation, ≤PN40, clean seawater, fuel, oil lines, moderate temp | High temperature steam lines, throttling service, slurry/contaminated seawater | Marine ball valves must be corrosion resistant (316SS/monel), often with packing for saltwater exposure |
| Gate Valve (marine standard) | Ball Valve (full bore), Lug Butterfly Valve (high corrosion grade) | Large diameter systems, low-frequency operation, on/off isolation | Frequent operation (wear issues), throttling, water hammer prone lines | Gate valves preferred for ballast water and firewater isolation; ensure flanges meet ship spec standards |
| Butterfly Valve (rubber/fabrics) | Triple-Offset Metal Seated Butterfly Valve, Ball Valve (limited) | Large lines, cooling seawater, firewater, when tight shutoff not critical | Fuel oil or boiler steam lines, throttling, high pressure (>PN40) | Triple offset designs resist corrosion, biofouling; rubber seats degrade in saltwater, verify chemical compatibility |
| Check Valve (swing or spring) | Flanged Wafer or Lift Check Valve | Non-return function in seawater lines, proper orientation, pressure limits | Vertical orientation with high pulsations, silting or marine growth risk | Essential for pump protection, prevent seawater backflow; regular inspection to prevent fouling |
| Globe Valve (marine spec) | Control Valve (pneumatic/hydraulic) | For flow regulation, injection lines, fuel dosing, compatible pressure/temperature | Using globe valve for on/off isolation only, poorly maintained automated valves | Marine globe valves sized for corrosion resistance and flow control; often actuated in engine rooms |
| Needle Valve | Globe Valve, Diaphragm Valve (low pressure) | For precise flow control in lubrication, chemical feed, steam tracing | High pressure slurry pipelines, emergency isolation | Needle valves critical for dosing; materials must resist sea chemicals and biofouling |
| Plug Valve (lubricated) | Ball Valve, Butterfly Valve (limited) | Simple on/off services in clean water or oil transfer lines | Marine bilge water, contaminated fuel or sludge lines | Plug valves need lubricant for marine conditions; may seize if unused |
| Pressure Relief Valve | Same size and rating valve | Emergency pressure protection, certified to marine safety codes | Replacing with isolation valves, undersized relief valves | SRVs critical for HVAC, fuel systems, boilers; must meet IMO and classification society standards |
| Diaphragm Valve (sanitary) | Ball Valve (sanitary rating), Pinch Valve | Clean potable water or sludge lines with low pressure requirements | High pressure steam, abrasive fluids, marine chemical injection | Sanitary valves used in food-grade water, potable water systems; ensure seal longevity against marine water |
| Electro-Hydraulic Actuated Valves | Same valve body with upgraded actuator | For remote operation, integrated control | Manual only systems with high frequency, or uncontrolled operation | Marine automation requires IP69K rated actuators and corrosion-resistant hardware |

REPLACEMETS POSSIBLE FOR OIL

| Original Valve Type | Can Replace With | Conditions When Replacement Is Feasible | When Replacement Is Not Advisable | Key Considerations |
| --- | --- | --- | --- | --- |
| Gate Valve | Ball Valve (full bore), Globe Valve, Plug Valve | On/off isolation duty, similar or higher pressure rating (API 6D class 150+), moderate flow rates, accessibility for maintenance | High frequency on/off cycling, throttling service, high-speed operation, erosion/corrosion prone fluids, safety-critical control points | Gate valves provide minimal pressure drop, reliable isolation but slow operation; ensure pressure rating matches system requirements |
| Ball Valve (API 6D) | Gate Valve, Plug Valve | Full bore flow, high-cycle on/off duty, moderate pressure and temperature, straightforward pipeline applications | Throttling applications, abrasive slurry, high temperature (>200°C) beyond seal rating, highly viscous fluids damaging seals | Full bore ball valves reduce pressure drop; seals must match fluid chemistry; side-entry or top-entry for maintenance critical |
| Globe Valve | Control Valve (automated), Gate Valve (isolation only) | Flow regulation and throttling required, moderate pressure and temperature within rating | On/off isolation only (use gate/ball instead), high cycle rapid operation (accelerated wear) | Globe valves specialized for flow control, higher pressure drop; automated variants common in process control loops |
| Check Valve (Swing/Silent) | Lift Check Valve, Spring Check Valve, Dual Plate Check Valve | Backflow prevention required, compatible flow velocity (≥0.5 m/s), vertical/horizontal installation | Improper installation (wrong orientation), pulsating flow, slurry with solids or corrosion-prone fluids | Check valves prevent reverse flow; ensure proper orientation and material compatibility to prevent failure |
| Control Valve (Automated) | Upgraded actuator, same valve body, Globe Valve variants | Process control with pressure/flow modulation, matched design pressure and actuation requirements | Replacing with manual valves (loss of control), unmatched seal or pressure ratings, incompatible instrumentation | Control valves require precise sizing, leak tightness, actuation power; API and ASME certification usually mandatory |
| Plug Valve | Ball Valve, Gate Valve (isolation) | Low erosion slurry, on/off service, pressure rating matching, limited flow regulation | High erosive fluids causing wear, poorly maintained lubrication in plug valves, partial throttle operation | Plug valves are quick to operate, compact, but require proper lubrication and maintenance |
| Knife Gate Valve | Solid Wedge Gate Valve, Lug Gate Valve, Ball Valve (cautiously in clean water) | Slurry/sludge with high solids, manual on/off operation, moderate temperature and pressure | High frequency cycling, throttling applications, low solids or clean fluids where other valves preferred | Knife gate valves designed for solids, minimal obstruction when open; wear parts subject to high replacement rates |
| Pressure Relief Valve | Same type replacement, upgraded set pressure parts | Overpressure protection with appropriate relief capacity and set pressure | Substituting as isolation valve, undersized relief capacity, incompatible with process media | Pressure relief valves are safety-critical and must be selected per API 526 / API 2000 guidelines |